PROGRESSING CAVITY PUMPSPRIVATE 

Vertical
PART 1
GENERAL
1.01
DESCRIPTION


A.
SCOPE: This section specifies vertical positive displacement progressing cavity pumps, complete with electric motors, and all specified appurtenances, as shown on the plans and specified herein.


B.
TYPE: The pumping units shall be of the vertical positive displacement, progressing cavity type specifically designed for pumping the as specified waste water sludge.


C.
EQUIPMENT LIST



Item





Equipment Number 


Sludge Pump




     

D.
PERFORMANCE AND DESIGN REQUIREMENTS:



1.
Sludge handling pumps shall be specifically designed and selected for continuous duty pumping of wastewater sludge with the following properties:




Percent Solids



Up to 6%




Specific Gravity



     







Viscosity



     





Solids Size



     



pH




     



Temperature



     



2.
The pumps shall be of the compact, close-coupled design. The gear 




reducer shall be sized for a minimum service factor of 1.5 and designed 




with a thrust load capability of 150 percent of the actual thrust load. 




3.
The pumps, along with associated drive appurtenances, shall be mounted 




on common fabricated steel mounting plate. The mounting plate shall be 




bolted to the tank top or chamber. The pump shall be the length as shown 




in the plans.



4.
The pump discharge shall be above (below) the pump mounting plate as 



shown on the plans.




5.
The pump casing shall be equipped with an intermediate housing between 




the stator and discharge tube, which facilitates the rapid exchange of the 




rotor, stator or U-joint.




6.
The pumps shall be fitted with distance pins and a guide unit, which 




anchors the bottom of the pump to the tank bottom.




7.
Manufacturers must currently have installations for similar liquids in 




service for a minimum of three years. Manufacturers not named in this 




specification must also provide a pre-submittal package to the engineer 




no less than three weeks prior to the bid date for approval. The pre-




submittal package must include, at minimum, the following: dimensional 




drawing, performance curve, O&M manual, electrical/drive details, 




installation list (for the same liquids as specified) with minimum three 




contacts and phone numbers.

E.
OPERATING CONDITIONS: The vertical progressing cavity pumps shall have the following operating characteristics:

	PRIVATE 

Equipment

Service
	Rated

Capacity,

gpm.
	Maximum

total

Diff. pressure

psig
	Maximum/

minimum

pump speed,

rpm


	Discharge

port size,

in
	Minimum

motor

hp
	Submersible Depth

inches
	Drive

	Sludge Feed

High Flow

Low Flow


	

	


	

	

	

	

	 FORMCHECKBOX 
 Constant

 FORMCHECKBOX 
 Variable Speed




1.02
REFERENCES


A.
This section contains references to the following documents. They are part of this section as specified and modified. In case of conflict between the requirements of the section and those of the listed documents, the requirements of this section shall prevail.



Reference

Title


AGMA 6010-E-88
Spur, Helical, Herringbone, and Bevel Enclosed Drive



AGMA 6019-E-89
Gear Motors Using Spur, Helical, Herringbone, Straight Bevel, or Spiral Bevel Gears



AGMA 6023-A88
Design Manual for Enclosed Epicyclic Gear Drives

1.03
ENVIRONMENTAL CONDITIONS

A. Pumps to be provided under this section will be installed in the       Building. 


Environmental conditions are as described in Section      .

1.04
SUBMITTALS


A.
The following information shall be provided in accordance with Section      .



1.
Manufacturer's data including materials of construction and equipment weight.



2.
Predicted performance curves developed for the specific application. Performance curves shall plot speed, capacity, head, horsepower and efficiency required for the specified operating range.

3. Motor data as specified in Section      .
4. Universal joint warranty and statement verifying that the universal joints are rated for the discharge pressures of each application.



5.
A copy of this specification section with addenda updates, and all referenced sections with addenda updates, with each paragraph check marked to show specification compliance or marked to show deviations.

PART 2
PRODUCTS
2.01
ACCEPTABLE PRODUCTS

  
A.
Progressing cavity pumps shall be seepex Model BE.

2.02
MATERIALS

	PRIVATE 
Component
	Material

	Rotor
	AISI 316 Ti with Duktil coating

	Stator
	Buna

	Pump Body
	Steel

	Mechanical seals
	Burgmann MG1- Dw/G60Q1Q1VGG


2.03
EQUIPMENT


A.
ROTOR AND STATOR: Each pump shall be a one (two) stage design employing a convoluted rotor operating in a similarly convoluted stator. The convolutions shall be configured to form a cavity between the rotor and stator, which shall progress from the pump's inlet to discharge port with the operation of the rotor. The fit between the rotor and stator at the point of contact shall compress the stator material sufficiently to form a seal and to prevent leakage from the discharge back to the inlet end of the pumping chamber. The stator shall be molded with a seal integral to the stator elastomer preventing the metal stator tube and the bonding agent from the elastomer from contacting the pumped liquid. Gaskets or "O" rings may not be used to form this seal. Stators for sludge pumps shall have Buna elastomer. The sludge pump rotors shall be constructed of AISI 316 Ti. Additionally the sludge pump rotors shall have a chromium nitride coating (Duktil) with a hardness of 1250 Vickers and a minimum thickness of 


200 µm (.008"). Hard chrome plating or ceramic coatings are not acceptable due to the ease at which this coating will crack and the lack of diffusion into the rotor base metal. 

B.
ROTOR AND DRIVE TRAIN: The rotor drive train shall be warranted for one (1) year from acceptance and shall consist of the following:



1.
Each pump rotor shall be driven through a positively sealed and lubricated pin joint. The pin joint shall have replaceable bushings, constructed of air-hardened tool steel of 57-60 HRc, in the rotor head and coupling rod. The pin shall be constructed of high speed steel, air hardened to 60-65 HRc. The joint shall be grease lubricated with a high temperature (450 F), PTFE filled synthetic grease, covered with Buna N sleeve and positively sealed with hose clamps constructed of 304 stainless steel. A stainless steel shell shall cover the rotor sided universal joint assembly to protect the elastomer sleeve from being damaged by tramp metals or glass. The universal joints shall carry a separate warranty of 10,000 operating hours. This warranty shall be unconditional in regards to damage or wear. Universal joint shall be positively sealed and warranted not to allow intrusion of the pumped product into the universal joint at the rated discharge pressure for the application.

C.
CASING: A 150-pound (ANSI B16.5) raised face flanged connection shall be provided at the discharge port in the size and location as shown in the plans.


D.
SHAFT SEALS AND BEARINGS: Each pump shall be provided with oil lubricated thrust and radial bearings located in the gear motor, designed for all loads imposed by the specified service. Shaft shall be sealed using a single-acting mechanical seal as specified in 2.02. The shaft shall be solid through the mechanical seal area, but of a two part design which allows the mechanical seal and all other wetted rotating parts to be removed from the pump without disassembly of the pump or gear motor bearings. Mechanical seals shall be with solid silicon carbon faces with 316 stainless steel metal parts and Viton elastomers. Pump manufacturer shall supply with each pump a seal water quench system comprised of a pot and all required fittings needed for a complete system. 


E.
MOTOR AND DRIVE UNIT: 


1.

Gear motors or gear reducers shall be designed in accordance with AGMA 6019-E (Class II). Unless otherwise noted, motors shall be energy-efficient, TEFC motors in accordance with Section      .



2.
Pumps that require adjustable speed drives (ASDs) are noted in paragraph 1.01 E. ASDs shall be constant torque type as specified in Section      . For ASD-driven units, the pump supplier shall be responsible for the provision of the fixed reduction between the motor and pump. The reduction ratio shall be that required to operate the pump at its maximum operating speed when the motor is operating at its nominal rated full speed in accordance with the schedule in paragraph 1.01 E. ASD-driven units may be operated at up to 90 Hz at the maximum speed.

2.04
PRODUCT DATA


A.
The following information shall be provided in accordance with Section      :



1.
Mill certifications confirming hardness of rotor.



2.
Applicable operation and maintenance information specified in Section      .



3.
Motor data as specified in paragraph      .



4.
Installation certification Form       as specified in Section      .



5.
Training certification Form       as specified in Section      .

2.05
STANDBY COMPONENTS


A.
One set of special tools shall be provided to service the pumps. In addition, the following shall be provided for each pump size (as appropriate for type of drive provided):




1 – stator assembly 




1 – rotor




1 – set connecting rod joint assemblies




1 – mechanical seal


B.
Standby components shall be tagged and stored in accordance with provisions of Section      .

PART 3
EXECUTION
3.01
INSTALLATION


A.
The pumps shall be installed as specified and in accordance with manufacturer's written recommendations. The installation and initial operation of all components shall be certified on Form       as specified in Section      .

3.02
TESTING


A.
After completion of installation, the pumps shall be completely tested to demonstrate compliance with operating requirements as specified.

PART 4 
CERTIFICATION

4.01
Description
A.         Consideration will be given only to products of manufacturers who can demonstrate that their equipment fully complies with all requirements of the specifications and contract documents.  The equipment shall be supplied by a firm which has been regularly engaged in the design, fabrication, assembly, testing, start-up, and service of progressive cavity pumps, of the same model and size as proposed, operating in the U.S., with similar materials, for a period of not less that ten (10) years prior to the bid date of this contract.  To insure that the highest standards are met each bidder shall be certified to ISO 9001 quality standards as a progressive cavity pumps manufacturer in the United States.  The bidder shall submit data to substantiate the manufacturers experience in accordance with the contract documents.
B. If a bidding progressive cavity pump manufacturer does not have a formal quality system in place, or documentation to prove so, a performance/maintenance bond in the amount of 100% of the installed price (including equipment, labor, piping, and wiring associated with the equipment covered under this specification) shall be included in the bid proposal.  The bond should be made out to the owner for 100% of the amount bid, and shall be in force for a minimum of five (5) years from the date of first beneficial use of the equipment.  The five (5) year minimum is to cover all warranties listed under this specification.
END OF SECTION

