PROGRESSING CAVITY PUMPS 

Dewatered Sludge

PART 1
GENERAL
1.01
DESCRIPTION


A.
SCOPE: This section specifies positive displacement progressing cavity pumps, complete with electric motors, and all specified appurtenances, as shown on the plans and specified herein.


B.
TYPE: The pumping units shall be of the positive displacement, progressing cavity type specifically designed for pumping the as specified liquids.


C.
EQUIPMENT LIST



Item





Equipment Number 


Transfer Pump




     

D.
PERFORMANCE AND DESIGN REQUIREMENTS:



1.
Sludge handling pumps shall be specifically designed and selected for continuous duty pumping of liquids with the following properties:




Percent Solids



Up to 28%




Specific Gravity



     







Viscosity



     



Solids Size



     





pH




     



Temperature



     


2.
The pumps shall be of the compact, close-coupled design. The gear 



reducer shall be sized for a minimum service factor of 1.5 and designed 



with a thrust load capability of 150 percent of the actual thrust load. 






3.
The pumps, along with associated drive appurtenances, shall be mounted 





on common fabricated steel base plates.



4.
Manufacturers must currently have installations for the same liquids in 



service for a minimum of three years. Manufacturers not named in this 



specification must also provide a pre-submittal package to the engineer 



no less than three weeks prior to the bid date for approval. The pre-



submittal package must include, at minimum, the following: dimensional 



drawing, performance curve, O&M manual, electrical/drive details, 



installation list (for the same liquids as specified) with minimum three 



contacts and phone numbers. Submittal of equipment that is either not 



named or pre-approved will be rejected.

E. OPERATING CONDITIONS: The progressing cavity pumps shall have the following operating characteristics:
	PRIVATE 

Equipment

Service
	Rated

Capacity,

gpm.
	Differential

Pressure

psi
	Maximum/

minimum

pump speed,

rpm


	Discharge

port size,

in
	Minimum

motor

hp
	Hopper

Length

inches
	Drive

	Sludge Feed

High Flow

Low Flow


	

	


	

	

	

	

	 FORMCHECKBOX 
 Constant

 FORMCHECKBOX 
 Variable Speed




1.02
REFERENCES


A.
This section contains references to the following documents. They are part of this section as specified and modified. In case of conflict between the requirements of the section and those of the listed documents, the requirements of this section shall prevail.

.



Reference

Title


AGMA 6010-E-88
Spur, Helical, Herringbone, and Bevel Enclosed Drive



AGMA 6019-E-89
Gear Motors Using Spur, Helical, Herringbone, Straight Bevel, or Spiral Bevel Gears



AGMA 6023-A88
Design Manual for Enclosed Epicyclic Gear Drives

1.03
ENVIRONMENTAL CONDITIONS


A.
Pumps to be provided under this section will be installed inside the       Building. Environmental conditions are as described in Section      .

1.04
SUBMITTALS


A.
The following information shall be provided in accordance with Section      .



1.
Manufacturer's data including materials of construction and equipment weight.



2.
Predicted performance curves developed for the specific application. Performance curves shall plot speed, capacity, head, and horsepower required for the specified operating range.



3.
Motor data as specified in Section      .



4.
Universal joint warranty.



5.
A copy of this specification section with addenda updates, and all referenced sections with addenda updates, with each paragraph check marked to show specification compliance or marked to show deviations.

PART 2
PRODUCTS
2.01
ACCEPTABLE PRODUCTS

  
A.
Progressing cavity pumps shall be seepex Series BTE.

2.02
MATERIALS

	PRIVATE 
Component
	Material - Sludge Pumps

	Rotor
	316ss - Duktil Coated (1250 Vickers hardness) 

	Stator
	Buna N

	Pump Body
	Cast iron / Steel

	Shaft Sealing
	Packing


2.03
EQUIPMENT


A.
ROTOR AND STATOR: Each pump shall be a minimum two (four, eight) stage design employing a convoluted rotor operating in a similarly convoluted stator. The convolutions shall be configured to form a cavity between the rotor and stator, which shall progress from the pump's inlet to discharge port with the operation of the rotor. The fit between the rotor and stator at the point of contact shall compress the stator material sufficiently to form a seal and to prevent leakage from the discharge back to the inlet end of the pumping chamber. The stator shall be molded with a seal integral to the stator elastomer preventing the metal stator tube and the bonding agent from the elastomer from contacting the pumped liquid. Gaskets or "O" rings may not be used to form this seal. Stators for sludge pumps shall have Buna elastomer. The sludge pump rotors shall be constructed of 316 SS. Additionally the sludge pump rotors shall have a chromium nitride coating (Duktil) with a hardness of 1250 Vickers and a minimum thickness of 250 (m (.0108"). Hard chrome plating or ceramic coatings are not acceptable due to the ease at which this coating will crack and the lack of diffusion into the rotor base metal. 


B.
ROTOR AND DRIVE TRAIN: The rotor drive train shall be warranted for three (3) years from acceptance and shall consist of the following:



1.
Each pump rotor shall be driven through a positively sealed and lubricated pin joint. The pin joint shall have replaceable bushings, constructed of air-hardened tool steel of 57-60 HRc, in the rotor head and coupling rod. The pin shall be constructed of high speed steel, air hardened to 60-65 HRc. The joint shall be grease lubricated with a high temperature (450( F), PTFE filled synthetic grease, covered with Buna N sleeve and positively sealed with hose clamps constructed of 304 stainless steel. A stainless steel shell shall cover the rotor side universal joint assembly to protect the elastomer sleeve from being damaged by tramp metals or glass. The universal joints shall carry a separate warranty of 10,000 operating hours. This warranty shall be unconditional in regards to damage or wear.


C.
CASING: A 150 (300, 600) - pound (ANSI B16.5) flanged connection shall be provided at the discharge port. The discharge casings shall each be provided with a 3/8-inch (or larger) tap to permit installation of pressure instruments. The suction casing shall be fabricated from corrosion resistant steel plate and designed with a rectangular opening which is      ” by      ”. The suction casing shall incorporate an oversized and detachable “extension tube” between the hopper opening and the rotor and stator. A single helix ribbon-style auger shall run the entire length of the suction casing and the extension tube and shall transmit rotational movement from the drive shaft to the rotor. The ribbon-style auger and extension tube work in concert to apply additional shearing forces against thixotropic liquids to reduce the apparent viscosity of the material, minimize air entrainment and improve the volumetric efficiency of the pumping elements. The ribbon-style auger diameter and pitch shall be designed to transport no less than 300% of the rated capacity of the pumping elements.

D.
SHAFT SEALS AND BEARINGS: Each pump shall be provided with oil lubricated thrust and radial bearings, located in the gear motor, designed for all loads imposed by the specified service. The shaft shall be solid through the stuffing box area, but of a two part design which allows the packing and all other wetted rotating parts to be removed from the pump without disassembly of the pump or gear motor bearings. The drive shaft shall be coated in the packing contact area with the same chromium nitride material of 1250 Vickers hardness that is used as the rotor coating. The stuffing box shall be of ample depth for 5 rings of packing and be provided with lantern rings and seal water flush connections. The lantern ring shall be split for convenient removal. The stuffing box housing shall be drilled and tapped for water flush connections. 
E.
PACKING FLUSH ASSEMBLY: The pump manufacturer shall supply components for a complete packing flush assembly including: solenoid valve, ball valve, pressure regulator, 2½" gauge with snubber, 'y' strainer, needle valve and appropriate tees and nipples. All wetted parts shall be brass or 316 stainless steel.

F.
ANTIREVERSAL HOLDBACK. Each main pump gearbox shall be fitted with a differential friction-type holdback designed to prevent reversal of flow when the pump is not in operation. The holdback shall be fitted as an integral component of the main pump gear drive and the unit will be adequately protected against the entrance of dust, dirt and moisture. Anti-reversal holdbacks shall be adequately sized for the specified service.


G.
MOTOR AND DRIVE UNIT: 



1.
Gear motors or gear reducers shall be designed in accordance with AGMA 6019-E (Class II). Unless otherwise noted, motors shall be energy-efficient, TEFC motors in accordance with Section      .



2.
Pumps that require adjustable speed drives (ASDs) are noted in paragraph 1.01 E. ASDs shall be constant torque type as specified in Section      . For ASD-driven units, the pump supplier shall be responsible for the provision of the fixed reduction between the motor and pump. The reduction ratio shall be that required to operate the pump at its maximum operating speed when the motor is operating at its nominal rated full speed in accordance with the schedule in paragraph 1.01 E. ASD-driven units may be operated at up to 90 Hz at the maximum speed.

2.04
ACCESSORIES:


A.
RUN DRY PROTECTION: The stator shall be fitted with a sensor sleeve and thermistor sensor. A controller shall also be provided and shall be installed by the contractor in the motor control center. The controller shall monitor the stator temperature and activate a shutdown and alarm sequence if the stator temperature reaches the adjustable limit on the controller. The controller shall include a manual local and remote reset function. Input to the controller shall be 1x115VAC/60 Hz.

B.
OVER PRESSURE PROTECTION: Each pump unit shall be supplied with a silicone-filled isolation ring with a dual mounted gauge and single point pressure switch. The pressure ranges for the switch and gauge shall be selected specifically for each specified service. The isolation ring shall be mounted between ANSI flanges, be sized according to the discharge pipe as shown on the plans, and be constructed with a carbon steel body and fittings with a Buna sleeve. The switch shall be SPDT, NEMA 4.

2.05
PRODUCT DATA


A.
The following information shall be provided in accordance with Section      :



1.
Mill certifications confirming hardness of rotor.



2.
Applicable operation and maintenance information specified in Section      .



3.
Motor data as specified in Section      .



4.
Installation certification Form       as specified in Section      .



5.
Training certification Form       as specified in Section      .

2.06
STANDBY COMPONENTS


A.
One set of packing tools shall be provided to service the pumps. In addition, the following shall be provided for each pump size (as appropriate for type of drive provided):




1 – stator assembly with TSE sensor sleeve




1 – rotor




1 – set universal joint assemblies




1 – set packing


B.
Standby components shall be tagged and stored in accordance with provisions of Section      .

PART 3
EXECUTION
3.01
INSTALLATION


A.
The pumps shall be installed as specified and in accordance with manufacturer's written recommendations. The installation and initial operation of all components shall be certified on Form       as specified in Section      .

3.02
TESTING


A.
After completion of installation, the pumps shall be completely tested to demonstrate compliance with operating requirements as specified.

PART 4 
CERTIFICATION

4.01
Description

A.         Consideration will be given only to products of manufacturers who can demonstrate that their equipment fully complies with all requirements of the specifications and contract documents.  The equipment shall be supplied by a firm which has been regularly engaged in the design, fabrication, assembly, testing, start-up, and service of progressive cavity pumps, of the same model and size as proposed, operating in the U.S., with similar materials, for a period of not less that ten (10) years prior to the bid date of this contract.  To insure that the highest standards are met each bidder shall be certified to ISO 9001 quality standards as a progressive cavity pumps manufacturer in the United States.  The bidder shall submit data to substantiate the manufacturers experience in accordance with the contract documents.

B.
If a bidding progressive cavity pump manufacturer does not have a formal quality system in place, or documentation to prove so, a performance/maintenance bond in the amount of 100% of the installed price (including equipment, labor, piping, and wiring associated with the equipment covered under this specification) shall be included in the bid proposal.  The bond should be made out to the owner for 100% of the amount bid, and shall be in force for a minimum of five (5) years from the date of first beneficial use of the equipment.  The five (5) year minimum is to cover all warranties listed under this specification.

END OF SECTION

