SODIUM HYPOCHLORITE PUMPS

PROGRESSING CAVITY
PART 1
GENERAL
1.01
DESCRIPTION


A.
SCOPE: This section specifies positive displacement progressing cavity pumps, complete with electric motors, and all specified appurtenances, as shown on the plans and specified herein.


B.
TYPE: The pumping units shall be of the positive displacement, progressing cavity type specifically designed for pumping sodium hypochlorite solutions, as specified. 


C.
EQUIPMENT LIST



Item





Equipment Number 


NaOCl Feed Pump #1



     


NaOCl Feed Pump #2



     

D.
PERFORMANCE AND DESIGN REQUIREMENTS:



1.
Pumps shall be specifically designed and selected for continuous duty pumping of sodium hypochlorite with the following properties:




Percent Concentration

12.5 %




2.
The pumps shall be of the compact, close-coupled design. The gear 





reducer (if required) shall be sized for a minimum service factor of 1.5 and 





designed with a thrust load capability of 150 percent of the actual thrust 





load. 




3.
The pumps, along with associated drive appurtenances, shall be mounted 





on common fabricated steel base plates.



4.
Manufacturers not named in this specification must provide a pre-




submittal package to the engineer no less than three weeks prior to the 




bid date for approval. The pre-submittal package must include, at 




minimum, the following: dimensional drawing, performance curve, O&M 




manual, electrical/drive details, sodium hypochlorite installation list with 




minimum three contacts and phone numbers.

E.
OPERATING CONDITIONS: The progressing cavity pumps shall have the following operating characteristics:

	PRIVATE 

Equipment

Service
	Rated

Capacity,

gpd
	Differential Pressure

psi
	Maximum/

minimum

pump speed,

rpm


	Suction and discharge

port size,

NPT – in
	Minimum

motor

hp
	Drive

	Feed Pump #1

High Flow

Low Flow


	     
     
	     
     
	600

      
	1” - ½”

     
	0.5
	AC Motor

Fixed

Reduction

VFD

	Feed Pump #2

High Flow

Low Flow


	     
     
	     
     
	600

     

	1” - ½”

     
	0.5
	AC Motor

With Integral

Controller


1.02
REFERENCES


A.
This section contains references to the following documents. They are part of this section as specified and modified. In case of conflict between the requirements of the section and those of the listed documents, the requirements of this section shall prevail.



Reference

Title


AGMA 6010-E-88
Spur, Helical, Herringbone, and Bevel Enclosed Drive



AGMA 6019-E-89
Gear Motors Using Spur, Helical, Herringbone, Straight Bevel, or Spiral Bevel Gears



AGMA 6023-A88
Design Manual for Enclosed Epicyclic Gear Drives

1.03
ENVIRONMENTAL CONDITIONS


A.
Pumps to be provided under this section will be installed in the       Building. Environmental conditions are as described in Section      .

1.04
SUBMITTALS


A.
The following information shall be provided in accordance with Section      .



1.
Manufacturer's data including materials of construction and equipment weight.



2.
Predicted performance curves developed for the specific application. Performance curves shall plot speed, capacity, head, and horsepower required for the specified operating range.



3.
Motor data as specified in paragraph      .



4.
Universal joint warranty.



5.
A copy of this specification section with addenda updates, and all referenced sections with addenda updates, with each paragraph check marked to show specification compliance or marked to show deviations.

PART 2
PRODUCTS
2.01
ACCEPTABLE PRODUCTS

  
A.
Progressing cavity pumps shall be seepex, Inc. Series MD.

2.02
MATERIALS

	PRIVATE 
Component
	Material - NaOCl Pumps

	Rotor
	Titanium

	Stator
	EPDM

	Pump Body
	HDPE 

	Shaft
	Titanium

	Mechanical Seal
	John Crane Type 1 Titanium


2.03
EQUIPMENT


A.
ROTOR AND STATOR: Each pump shall be a minimum two-stage design employing a convoluted rotor operating in a similarly convoluted stator. The convolutions shall be configured to form a cavity between the rotor and stator, which shall progress from the pump's inlet to discharge port with the operation of the rotor. The fit between the rotor and stator at the point of contact shall compress the stator material sufficiently to form a seal and to prevent leakage from the discharge back to the inlet end of the pumping chamber. The stator shall be molded with a seal integral to the stator elastomer preventing the metal stator tube and the bonding agent from the elastomer from contacting the pumped liquid. Gaskets or "O" rings may not be used to form this seal. Stators for sodium hypochlorite pumps shall have EPDM elastomer. The sodium hypochlorite pump rotors shall be constructed of titanium. 

B. ROTOR AND DRIVE TRAIN: The rotor drive train shall be warranted for one (1) year from acceptance and shall consist of the following:



1.
Each pump rotor shall be driven through a positively sealed and lubricated pin joint. The pin shall be constructed of high speed steel, air hardened to 60-65 HRc. The joint shall be grease lubricated with a high temperature (450° F), PTFE filled synthetic grease, covered with EPDM sleeve and positively sealed with hose clamps constructed of Hastelloy. The shaft under the mechanical seal shall be constructed of titanium.


C.
CASING: NPT connections shall be provided at both the inlet and discharge ports. Casings shall be constructed of high-density polyethylene (HDPE). 


D.
SHAFT SEALS AND BEARINGS: Shaft shall be sealed using a single-acting mechanical seal constructed of EPDM elastomers, silicon carbide or ceramic faces, and either Halar coated Hastelloy, or titanium metal parts. The shaft shall be solid through the mechanical seal area, but of a two part design which allows the mechanical seal and all other wetted rotating parts to be removed from the pump without disassembly of the pump or gear motor (if required) bearings. Bearings shall be located in the motor or gear motor as required and shall be designed to adequately withstand all radial and thrust loads imposed by the pump at the service conditions.


E.
MOTOR AND DRIVE UNIT: 



1.
Gear motors or gear reducers (if required) shall be designed in accordance with AGMA 6019-E (Class II). Unless otherwise noted, motors shall be energy-efficient motors in accordance with Section      .



2.
AC MOTOR: Pumps that require adjustable speed drives (ASDs) are noted in paragraph 1.01 E. Adjustable speed drives shall be constant torque type as specified in Section      . For ASD-driven units, the pump supplier shall be responsible for the provision of the fixed reduction between the motor and pump. The reduction ratio shall be that required to operate the pump at its maximum operating speed when the motor is operating at its nominal rated full speed in accordance with the schedule in paragraph 1.01 E. ASD-driven units may be operated at 90 Hz at the maximum speed.




OR




AC MOTOR WITH INTEGRAL VARIABLE DRIVE: Motor shall be ½ Hp, 600 to 20 rpm gear motor, or ¾ Hp 1750 t0 170 rpm motor, TEFC High Efficiency, 115V 60Hz with power cord. The controller housing shall be NEMA 4 and integral to the motor. The integral motor/controller shall have a minimum 6 Ft. cord with AC plug, single phase, 115 VAC, and be designed for up to a 30:1 turndown without an encoder. The controller shall have the following as a minimum: 10-turn speed potentiometer and HOA switch. In addition, the controller shall have the following Turck FP-5 connection inputs: 4-20mA control signal, AC flow switch, and AC pressure switch. The controller inputs can, in lieu of an AC flow switch, provide the power to, and inhibit connections for, the run dry protection controller specified in Section 2.04. In this case, the run dry controller is to be mounted by the contractor.

2.04
ACCESSORIES: 


A.
RUN DRY PROTECTION (In Lieu of AC Flow Switch)


Except sizes 0005, 0015, 003


The stator shall be fitted with a sensor sleeve, with all wetted components of titanium, and thermistor sensor. A controller shall also be provided and shall be installed by the contractor. The controller shall monitor the stator temperature and activate a shutdown and alarm sequence if the stator temperature reaches the adjustable limit on the controller. The controller shall include a manual local and remote reset function. Input to the controller shall be 1x115VAC/60 Hz. 

B.
AC FLOW SWITCH (In lieu of Run dry protection)



A low flow switch shall be provided and fitted into a “tee” in the discharge piping of the pump. The low flow switch shall be the SI106 from IFM Efector, model SID10ADBFKOW/LS.  Wetted parts shall be  AISI 316, except when titanium is required due to the carrion of the pumped fluid.  Power requirement shall be 120 VAC and the instrumentation connector shall be the Turck FP-5, ½” 20UNF 2A. A Turck connector cord of sufficient length shall be to allow interface between the IVD controller and the low flow switch shall be provided.

C.
AC INDICATING PRESSURE SWITCH


An indicating pressure switch shall be provided and fitted into a “tee” in the discharge piping of the pump.  The low flow switch shall be from IFM Efector, model PN4223.  Wetted parts shall be AISI 316.  Power requirement shall be 120 VAC and the instrumentation connector shall be the Turck FP-5, ½” 20UNF 2A. A Turck connector cord of sufficient length shall be to allow interface between the IVD controller and the low flow switch shall be provided.

2.05
PRODUCT DATA


A.
The following information shall be provided in accordance with Section      :



1.
Applicable operation and maintenance information specified in Section      .



2.
Motor data as specified in Section      .



3.
Installation certification Form       as specified in paragraph      .



4.
Training certification Form      as specified in paragraph      .

2.06
STANDBY COMPONENTS


A.
One set of special tools shall be provided to service the pumps. In addition, the following shall be provided for each pump size:




1 – stator assembly (with TSE sensor sleeve as required)




1 – rotor




1 – set universal joint assemblies




1 – mechanical seal


B.
Standby components shall be tagged and stored in accordance with provisions of paragraph      .

PART 3
EXECUTION
3.01
INSTALLATION


A.
The pumps shall be installed as specified and in accordance with manufacturer's written recommendations. The installation and initial operation of all components shall be certified on Form       as specified in Section      .

3.02
TESTING


A.
After completion of installation, the pumps shall be completely tested to demonstrate compliance with operating requirements as specified.

PART 4 
CERTIFICATION

4.01
Description

A.         Consideration will be given only to products of manufacturers who can demonstrate that their equipment fully complies with all requirements of the specifications and contract documents.  The equipment shall be supplied by a firm which has been regularly engaged in the design, fabrication, assembly, testing, start-up, and service of progressive cavity pumps, of the same model and size as proposed, operating in the U.S., with similar materials, for a period of not less that ten (10) years prior to the bid date of this contract.  To insure that the highest standards are met each bidder shall be certified to ISO 9001 quality standards as a progressive cavity pumps manufacturer in the United States.  The bidder shall submit data to substantiate the manufacturers experience in accordance with the contract documents.

B.
If a bidding progressive cavity pump manufacturer does not have a formal quality system in place, or documentation to prove so, a performance/maintenance bond in the amount of 100% of the installed price (including equipment, labor, piping, and wiring associated with the equipment covered under this specification) shall be included in the bid proposal.  The bond should be made out to the owner for 100% of the amount bid, and shall be in force for a minimum of five (5) years from the date of first beneficial use of the equipment.  The five (5) year minimum is to cover all warranties listed under this specification.

END OF SECTION
